Title : How to use the COM3 on the ADAM-5511 ?

Description : 

COM3 can only be used by access the rigister directly : 
Program Port
FF80h : Serial Port Control
FF82h : Serial Port Status
FF84h : Serial Port Transmit Data
FF86h : Serial Port Receive Data
FF88h : Serial Port Baud Rate Divisor


Title : How to run simu5000.exe and access with ADAM-4000/5000 utility?

Description :

1, Set all dip-switch to off and boot the ADAM-5511 then it will execute simu5000.exe automatically
2, Wait around 7 sec and you can see the LED become only the COMM is ˇĄonˇ¦. That means ready.
3, Connect PC to the program port of 5511 with direct through cable.
4, Use the ADAM-4000/5000 utility V1.3 and set baud-rate as 9600 N-8-1.
Then you can configure the modules with the ADAM-4000/5000 utility


Title : Accessing with ADAM-5511 widows utility (1) 

Description :

1, Set the ID of 5511 as NOT zero and boot the ADAM-5511 then it will execute the userˇ¦s program automatically
2, Wait around 7 sec and you can see the LED become:
PWR: ˇĄonˇ¦; RUN: ˇĄblinkingˇ¦;COMM: ˇĄoffˇ¦; BATT: ˇĄoffˇ¦
3, Use ADAM-4K5K Utility V1.3 to read ADAM-5511
At this time ADAM-5511 can be accessed through COM1 and COM2
When we use COM2
1, Make sure your com port is RS-485 mode or you are using ADAM-4520 as converter.
2, Check the setting of ADAM-4520, and make sure the SW1 is set as 11 bits (the default setting is 10 bits) and the baud-rate is correct.
3, Boot ADAM-5511 and wait until the LEDs are stable


Title : Accessing with ADAM-5511 widows utility (2)

Description : If we want to use COM1
1, Turn the SW6 to ˇĄonˇ¦
2, Use null modem cable connect PC to COM1
3, Make sure the baud-rate is correct
4, Boot ADAM-5511 and wait until the LEDs are stable and you can find the 5511 with its windows utility


Title : How to run simu5000.exe and access with ADAM-4000/5000 utility?

Description :

1, Set all dip-switch to off and boot the ADAM-5511 then it will execute simu5000.exe automatically
2, Wait around 7 sec and you can see the LED become only the COMM is ˇĄonˇ¦. That means ready.
3, Connect PC to the program port of 5511 with direct through cable.
4, Use the ADAM-4000/5000 utility V1.3 and set baud-rate as 9600 N-8-1.
Then you can configure the modules with the ADAM-4000/5000 utility


PAGE  
1

